## Sheet1
	min	max
The panels
Efficiency of the solar panels η	0,18	0,12
Average day time power demand Pday	25	35	kW, for ten hours
Average night time power demand Pnight	10	15	kW, for 14 hours
Energy use per day W24h	390	560	kWh
Average insolation psun (Jan, Aug)	6,3	4,2	kWh/m2/day
required panel power Ppanels	39	56	kW, assuming 10 hour sun
Required panel area A	344	1111	m2

The batteries
dark time energy consumption Wdark	140	210	kWh
Battery bank (6V) capacity C	23333	35000	Ah
Number of batteries	13	19	battery: 6V, 1800 Ah, 350kg, 0,14m3
weight of batteries	4537	6806	kg
Volume of batteries	1,8	2,7	m3

Prices
(34 panels of 240pW for $12000)	1,07 €		I do not quite understand the peak watts
Panels (1€/W – 2€/W)	39 000 €	112 000 €
Batteries	24 954 €	37 431 €
Inverter etc. (50 kW)	8 000 €	12 000 €
A small generator (20kW – 40kW)	4 000 €	8 000 €
	75 954 €	169 431 €

A reference solar system (3kW, 5000€)	65 000 €	93 333 €

All the power from NEPA			not available in practise
power	0,0170 €	0,0960 €	€/kw
fixed cost	0 €	590 €	€/month
Annual cost	2 420 €	26 702 €

Power from the generators
Fuel